## BOM With Clarififcations
2) MS - Medium Pressure Steam ( 196 Degree C , 3 Bar )-Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
| Supply and Installation of Pressure Safety Valve | --- | Nos | 1 | Specification Required
8 | Supply and Installation of Three way Manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 1 | Drawing Required for Threeway Manifold
9 | Supply and Installation of Temperature Transmitter | PT100 Type,B Class with Three wires Completer with head Transmitter ,4.20 Ma output,Minimum IP55 Protection,Connection to Piping and Neccessary Accessories for the Proper Installation) | Nos | 1
11 | Supply and Installation of Pressure Transmitter | < 0.5 % Measurement Error on Full scale,AI 203 Membrane,4.20 Ma output,Minimum IP 65 Degree of Protection,and Connection to Piping | Nos | 1
3) LS-Low Pressure Steam ( 60 Degree C , 0.2 Bar )-Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
18 | Supply and Installation of Three way Manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 1 | Drawing Required
19 | Supply and Installation of Pressure Gauge | Nominal Diamter : 4'',Stainless steel bourdon spring Sensing Element,Class 1 Accuracy ,Stainless steel movement and Case | Nos | 1
4) BW - Boiler Feed Water ( 105 Degree C, 44.5 Bar )-Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
24 | Supply and Installation of Interception Globe Valve | 1 1/2 '' Globe Valve, Ductile Iron Body,Stainless steel Disc,PTFE Seal,ANSI 400 Flanged Connections | Nos | 1
25 | Supply and Installation of Interception Globe Valve | 2'' Globe Valve, Ductile Iron Body,Stainless steel Disc,PTFE Seal,ANSI 400 Flanged Connections | Nos | 1
26 | Supply and Installation of Interception Globe Valve | 4'' Globe Valve, Ductile Iron Body,Stainless steel Disc,PTFE Seal,ANSI 400 Flanged Connections | Nos | 7
27 | Supply and Installation of Check Valve | 4'' Check Valve with Double Clapper,Ductile Iron body,ANSI 400 Wafer connections | Nos | 2
28 | Supply and Installation of Y Strainer | 1 1/2'' Y Strainer,Ductile iron Y Strainer,Stainless steel Basket,ANSI 400 Flanged Connections | Nos | 1
29 | Supply and Installation of Y Strainer | 4'' Y Strainer,Ductile iron Y Strainer,Stainless steel Basket,ANSI 400 Flanged Connections | Nos | 2
30 | Supply and Installation of Anti vibration Joint | 4'' Anti vibration Joint,Neoprene Body,ANSI 400 Flanged Connections | Nos | 4
31 | Supply and Installation of Flow Control Valve | 2'' Flow Control valve,Globe Valve for Manual regulation,Ductile Iron Body,Stainless steel Disc,Graphite Seal,ANSI 400 Flanged connections | Nos | 1
32 | Supply and Installation of Pneumatic Flow Control Valve | 1 1/2 '' Pneumatic Flow control valve,Globe valve for Automatic flow regulation ,Pneumatic Actuator,Limit Switches,Ductile Iron body,Stainless steel disc,Grapthite Seal,ANSI 400 Flanged connections | Nos | 1
33 | Supply and Installation of Pneumatic Flow Control Valve | 2 '' Pneumatic Flow control valve,Globe valve for Automatic flow regulation ,Pneumatic Actuator,Limit Switches,Ductile Iron body,Stainless steel disc,Grapthite Seal,ANSI 400 Flanged connections | Nos | 1
34 | Supply and Installation of Three way Manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 4 | Drawing Required for Threeway Manifold
35 | Supply and Installation of Process Thermometer | Nominal Diamter 4'',Spiral Bimettallic Sensing Element,Class 1 Accuracy,Stainless steel case,Every angle type | Nos | 1
36 | Supply and Installation of Temperature Transmitter | PT 100 Type,B Class with Three wires with Head transmitter,4.20 Ma Output,Minimum IP 55 Degree of Protection | Nos | 1
37 | Supply and Installation of Thermowell with Threaded connections | Suit at site | Nos | 2 | Drawing required for Thermowell
38 | Supply and Installation of Pressure Gauge | Nominal Diamter 4'',Stainless steel bourdon spring Sensing element,Class 1 accuracy,Stainless steel movement and case | Nos | 2
39 | Supply and Installation of Pressure transmitter | 0.5 % Measurement Error on full Scale,AI 203 Membrane,4.20 mA output,Minimum IP 65 Degree of Protection | Nos | 2
5) HW - Hot Water ( 60 Degree C, 0.2 Bar )-Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
47 | Supply and Installation of Interception Globe valve | 4'' Intereception Globe Valve,Ductile iron body,Stainless steel Disc,PTFE Seal,ANSI 150 Flanged connections, | Nos | 4
48 | Supply and Installation of Check Valve | 4'' Check valve for Double clapper,Ductile Iron body,ANSI 150 Wafer connections, | Nos | 1
49 | Supply and Installation of Flow Control Valve | 4'' Globe valve for Manual Regulation,Ductile Iron body,Stainless steel Disc,Graphite Seal,ANSI 150 Flanged connections | Nos | 2
50 | Supply and Installation of Pneumatic flow control valve | 1 1/2'' Globe valve for Automatic Regulation,Pneumatic Actuator,Limite Switches,Ductile Iron Body,Stainless steel disc,Grphite Seal,ANSI 150 Flanged connections | Nos | 1
51 | Supply and Installation of Threeway manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 4
52 | Supply and Installation of Pressure Gauge | Nominal Diamter : 4'',Stainless steel bourdon spring Sensing Element,Class 1 Accuracy ,Stainless steel movement and Case | Nos | 3
53 | Supply and Installation of Pressure Transmitter | 0.5 % Measurement Error on full scale,AI 203 Membrane,4.20 Ma Output,Minimum IP 65 Degree of Protection | Nos | 1
54 | Supply and installation of Water volume meter | Woltman type pulse flow meter and calculation flow meter | Nos | 1
6) CW - Cooling Water ( 45 Degree C, 4 Bar )-Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
61 | Supply and Installation of Manual Interception Valve | 1 1/2'' Manual Interception Butterfly Valve,Ductile Iron Body,Stainless steel Disc,EPDM Seal,Flanged ANSI 150 ,Lug Connection | Nos | 2
62 | Supply and Installation of Manual Interception Valve | 4'' Manual Interception Butterfly Valve,Ductile Iron Body,Stainless steel Disc,EPDM Seal,Flanged ANSI 150 ,Lug Connection | Nos | 4
63 | Supply and Installation of Manual Interception Valve | 16'' Manual Interception Butterfly Valve,Ductile Iron Body,Stainless steel Disc,EPDM Seal,Flanged ANSI 150 ,Lug Connection | Nos | 8
64 | Supply and Installation of Check valve | 16 '' Check Valve with Double Clapper,Ductile Iron body,ANSI 150 Wafer connections | Nos | 2
65 | Supply and Installation of Y Strainer | 16'' Ductile iron Y Strainer,Stainless steel basket,ANSI 150 Flanged Connections | Nos | 2
66 | Supply and Installation Anti vibrating Joint | 16'' Anti vibration Joint,Neoprene Body,ANSI 150 Flanged Connections | Nos | 4
67 | Supply and Installation of Threeway manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 8
68 | Supply and Installation of Spiral Thermometer | Nominal Diameter 4 '',Spiral Bi metallic Sensing Element,Class 1 Accuracy,Stainless steel Case,Every angle type | Nos | 6
69 | Supply and Installation of Temperature Transmitter | PT 100 Type,B Class with Three wires with Head transmitter,4.20 Ma Output,Minimum IP 55 Degree of Protection | Nos | 4
70 | Supply and Installation of Thermowell with Threaded connections | Suit at site | Nos | 10
71 | Supply and Installation of Pressure Gauge | Nominal Diamter : 4'',Stainless steel bourdon spring Sensing Element,Class 1 Accuracy ,Stainless steel movement and Case | Nos | 6
72 | Supply and Installation of Pressure Transmitter | 0.5 % Measurement Error on full Scale,AI 203 Membrane,4.20mA output,Minimum IP 65 Deg of Protection | Nos | 2
7) DW - Demineralized Water ( 20 Degree C, 4 Bar )--Stainless steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
77 | Supply and Installation of Manual Interception Butterfly Valve | 1.5'' Butter Fly valve,Ductile Iron body,Stainless steel Disc,EPDM Seal,Flanged 150 ,Lug Connection | Nos | 7
78 | Supply and Installation of Check Valve | 1.5'' Check valve with Double Clapper,Ductile Iron body,ANSI 150 Wafer connections | Nos | 3
79 | Supply and Installation of Ball valve | 1.5'' Ball valve,Stainless steel Body,NPT F Threaded,ANSI 150 Connection | Nos | 1
80 | Supply and Installation of Flow control valve | 1 1/2'' Globe valve for Manual Regulation,Ductile Iron Body,Stainless steel Disc,Graphite Seal,ANSI 150 Flanged Connections | Nos | 1
81 | Supply and Installation of Automatic Flow control valve | 1 1/2'' Globe valve for Automatic flow regulation,Pneumatic Actuator,Limit switches,Ductile Iron body,Stainless steel Disc,Graphite Seal,ANSI 150 Flanged connnections | Nos | 1
82 | Supply and Installation of Autoclave with Membrane | Capacity : 2000 Litres,Maximum Working Pressure 5 Bar, Preload 5 Bar | Nos | 1 | Drawing Required
83 | Supply and Installation of Threeway manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 6
84 | Supply and Installation of Pressure Gauge | Nominal Diamter : 4'',Stainless steel bourdon spring Sensing Element,Class 1 Accuracy ,Stainless steel movement and Case | Nos | 3
85 | Supply and Installation of Pressure Transmitter | 0.5 % Measurement Error on full scale,AI 203 Membrane,4.20 Ma Output,Minimum IP 65 Degree of Protection | Nos | 3
86 | Supply and installation of Water volume meter | Woltman type pulse flow meter and calculation flow meter | Nos | 1
8) IW - Industrial Water ( 20 Degree C, 4 Bar )--Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
89 | Supply and Installation of Interception Butterfly Valve | 2'' Butterfly Valve,Ductile Iron body,Stainless steel Disc,EPDM Seal,Flanged ANSI 150 Connection, | Nos | 3
90 | Supply and Installation of Interception Butterfly Valve | 4'' Butterfly Valve,Ductile Iron body,Stainless steel Disc,EPDM Seal,Flanged ANSI 150 Connection, | Nos | 5
91 | Supply and Installation of Check Valve | 4'' Check Valve with Double Clapper,Ductile Iron body,ANSI 150 Wafer Connections | Nos | 3
92 | Supply and Installation of Globe Valve | 2'' Interception Globe Valve ,Ductile Iron body,Stainless steel Disc,PTFE Seal,ANSI 150 Flanged Connections, | Nos | 1
93 | Supply and Installation of Pneumatic Flow Control Valve | 2'' Globe valve for Automatic Flow regulation,Pneumatic Actuator,Limite Switches,Ductile iron body,Stainless steel disc,Graphite Seal,ANSI 150 Flanged Connections | Nos | 1
94 | Supply and Installation of Y Strainer | 4'' Ductile Iron Y Strainer,Stainless steel basket,ANSI 150 Flanged connections, | Nos | 3
95 | Supply and Installation of Threeway manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 1
96 | Supply and Installation of Water flow meter | Water flow meter with Calibration | Nos | 2 | Specification Required
9) AD-CHEMICAL ADDITIVES ( 20 Degree C, 4 Bar )--Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
100 | Supply and Installation of Poly ethylene Piping | HOLD
101 | Sand Blasting and Painting SA 2.5 | HOLD
10) YH-HOT DRAINAGES ( 300 Degree C, 40 Bar )--Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
102 | Supply and Installation of Interception Globe Valve | 3'' Globe valve,Ductile Iron Body,Stainless steel Disc,PTFE Seal,ANSI 300 Flange Connections | Nos | 1
103 | Supply and Installation of Interception Globe Valve | 4'' Globe valve,Ductile Iron Body,Stainless steel Disc,PTFE Seal,ANSI 300 Flange Connections | Nos | 2
11) YW-WATER DRAINAGES ( 60 Degree C, 4 Bar )--Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
109 | Supply and Installation of Temperature Transmitter | PT 100 Type,B Class with Three wires with Head transmitter,4.20 Ma Output,Minimum IP 55 Degree of Protection | Nos | 1
110 | Supply and Installation of Thermowell with Threaded connections | Suit at site | Nos | 1
12) CD-Condensate Piping ( 300 Degree C, 40 Bar )--Carbon Steel Piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
115 | Supply and Installation of Globe Valve | 4 '' Globe Valve,Ductile Iron body,Stainless steel Disc,PTFE Seal,ANSI 300 Flanged Connections | Nos | 4
116 | Supply and Installation of Check Valve | 4'' Check Valve with Double Clapper,Ductile Iron body,ANSI 300 Wafer Connections | Nos | 1
117 | Supply and Installation of Y Strainer | 4'' Ductile Iron Y Strainer,Stainless steel Basket,ANSI 300 Flanged connections | Nos | 1
118 | Supply and Installation of Steam Trap | 4'' Carbon Steel body,ANSI 300 Flanged connections | Nos | 1
119 | Supply and Installation of Flow Glass | 4'' Flow indicator,Carbon steel body with borosilicate Glass,ANSI 300 Flanged connections | Nos | 1
13) IA-Instrumental Air ( 20 Degree C)--Stainless steel piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
124 | Supply and Installation of Ball valve | 1'' ball valve,Stainless steel body,NPT F-F Threaded,ANSI 150 | Nos | 15
125 | Supply and Installation of Ball valve | 11/2'' ball valve,Stainless steel body,NPT F-F Threaded,ANSI 150 | Nos | 1
126 | Supply and Installation of Check Valve | 1'' Check Valve with Double clapper,Ductile Iron body,ANSI 150 Wafer connection | Nos | 3
127 | Supply and Installation of Solenoid Valve | 1'' Automatic Three way valve,Electrical Actuator,Positioner and Positioner transmitter, | Nos | 3
130 | Supply and Installation of Threeway manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 9
131 | Supply and Installation of Pressure Gauge | Nominal Diamter : 4'',Stainless steel bourdon spring Sensing Element,Class 1 Accuracy ,Stainless steel movement and Case | Nos | 7
132 | Supply and Installation of pressure Switch | Pressure Switch 0,1-1 Barg ,+0.5 Regulation Range ,SPDT Changeover Contract,AU/AG Contact,IP 65 Degree of Protection | Nos | 1
14) EX-Exhaust Gas ( 575 Degree C)--Stainless steel piping
S No | Description | Specification | UOM | Value | Requirements from Customer for Quotation | Remarks
137 | Supply and Installation of Expansion Joint | 84'' Expansion Joint | Nos | 6 | Drawing Required
138 | Supply and Installation of Threeway manifold | Body : AISI 316 L,NPT M/F 1/2'' Threaded and Including Fittings and Connection to Process and Instruments ,Supply of Nut and Bolts and All other Accessories Neccessary for the Proper Installation | Nos | 3 | Drawing Required
139 | Supply and Installation of Process Thermometer | Nominal Diamter 4'',Spiral Bimettallic Sensing Element,Class 1 Accuracy,Stainless steel case,Every angle type | Nos | 2
140 | Supply and Installation of Temperature Transmitter | PT 100 Type,B Class with Three wires with Head transmitter,4.20 Ma Output,Minimum IP 55 Degree of Protection | Nos | 2
141 | Supply and Installation of Pressure Gauge | Nominal Diamter : 4'',Stainless steel bourdon spring Sensing Element,Class 1 Accuracy ,Stainless steel movement and Case | Nos | 2
142 | Supply and Installation of Pressure Transmitter | 0.5 % Measurement Error on full scale,AI 203 Membrane,4.20 Ma Output,Minimum IP 65 Degree of Protection | Nos | 1